|  | Electrotechnology Printing Information Technology and Communications Industry Training Board 29 Drummond St Carlton VIC 3054 | Phone (03) 9654 1299 Facsimile (03) 9654 5299 |
| --- | --- | --- |

LICENSED ELECTRICIANS ASSESSMENT (LEA)

LET SAMPLE EXAMINATION

| Surname: |  |
| --- | --- |
| Given Names: |  |
| Date: |  |

- Personal notepads and paper are not permitted

The following reference books are permitted during the assessment session:

AS/NZS 3000:2000 Wiring Rules

AS/NZS 3000:2000 (Amendment 1:2001), (Amendment 2:2002) & Amendment 3:2003 Wiring Rules

AS/NZS 3000:2000 (Amendment 2:2002) Wiring Rules

# AS/NZS 3008.1.1:1998 Electrical Installations – Selection of Cables

AS/NZS 3012:2003 Electrical Installations – Construction and Demolition Sites

# AS/NZS 3017:2001 Electrical Installations Testing & Inspection Guidelines

Electricity Safety (Installations) Regulations 1999

Electricity Safety (Installations) (Amendment) Regulations 2001

Code of Practice for Safe Electrical Work - 1997 – OCEI

| Question | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Marks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total |  |

Candidates need to obtain 75% or more to pass this assessment.

| Reading Time: | 15 minutes |  |  |
| --- | --- | --- | --- |
| Working Time: | 2 hours |  | Assessor: _______________________ |
| At the end of this time you will be asked to stop. |

Candidate Signature:  _____________________________________________

WIRING RULES

In the THREE following Wiring Rules questions, you are required to:

- write the Wiring Rules Clause and/or Table number in the space provided

- the correct Wiring Rules Clause and Subclause must be given( eg. 3.5.2(b)(i))

- AS/NZS 3000:2000 Amendments 1, 2 & 3 have been applied to these questions

- indicate if your answer is from an Amendment

The correct answer to both parts must be given to obtain full marks.

Q 1.

What must be taken into account when alternative methods of calculating the maximum demand   (other than Appendix C ) are used for a particular electrical installation?

.................................................................................................................................................

.................................................................................................................................................

Wiring Rules Clause number...............................................................

[ 2 + 2 = 4 Marks ]

Q 2.

What are the requirements for earthing conductors that are jointed by soldering?

.................................................................................................................................................

.................................................................................................................................................

Wiring Rules Clause number..................................................

[ 2 + 2 = 4 Marks]

Q 3.

What is the difference between a PELV system and a SELV system?

.................................................................................................................................................

................................................................................................................................................

.................................................................................................................................................

Wiring Rules Clause number..................................................

[ 2 + 2 = 4 Marks]

CONSTRUCTION & DEMOLITION SITES

Q 4.

In this question relating to AS/NZS 3012, you are required to:

- write the Standard’s Clause number and/or Table number in the space provided

- the correct Clause and Sub-clause number must be given (eg 2.10.2(f))

The correct answer to both parts must be given to obtain full marks.

How can construction wiring be made readily distinguishable from permanent wiring other than by the use of iridescent yellow tape.

................................................................................................................................................

................................................................................................................................................

Standard Clause number..............................................

[ 3 + 3 = 6 Marks]

ELECTRICITY SAFETY (INSTALLATIONS) REGULATIONS 1999

Part 4 - Electrical Installation Work

Q 5.

Amendments to these Regulations have been incorporated in this question.

The correct answer to parts (i) and (ii) must be given to obtain full marks.

Write the complete Regulation & Sub-regulation number, if applicable, for part (ii) (eg 401 (e)(3)).

(i) Is apparatus for the control of electricity considered to be Electrical Equipment?

................................................................................................................................................

(ii) Regulation number.............................................................

[ 3 + 3 = 6 Marks ]

ELECTRIC SHOCK SURVIVAL

Q 6.

What effect may an electric shock have on a victim?

..................................................................................................................................

[ 2 Marks ]

INSTALLATION DEFECTS - NON  DOMESTIC

Q 7.

The drawing above shows the MAIN SWITCHBOARD of an industrial installation originating at the consumers mains and contains contraventions to the Wiring Rules.

It supplies a distribution board having a connected load with a calculated maximum demand of 100 A per phase and an automatically controlled 3 phase fire pump motor having a current rating of 20 A per phase.

The multi-core MIMS cables are installed spaced from the wall.

Assume the MIMS cables are earthed in accordance with the Wiring Rules and are capable of maintaining supply to the equipment even when exposed to fire and mechanical damage.

All fuses shown are HRC type.

Complete the table on the following page.

Q 7. continued.

Use the diagram on the previous page.

List FOUR different defects together with the contravened  Wiring Rules Clause/Table number in the table provided below.

Note: Only the first four defects will be considered.

| DEFECT DETAILS | WIRING RULE CLAUSE/TABLE No. |
| --- | --- |

[ 4 x (2+1) = 12 Marks ]

NEUTRAL CONDUCTOR DETERMINATION

Q 8.

The 3 phase submain conductors of a MEN connected commercial installation are V75 single core aluminium insulated cables installed in a non-metallic conduit in air.

The greater portion of  the load at the distribution board is connected between active and neutral conductors.

The submain active conductors are 95mm² and protected by a circuit breaker.

Determine the minimum cross sectional area of the neutral conductor.

All relevant Table numbers and calculations must be shown to obtain full marks.

Answer.........................................

[ 2+2+2 = 6 Marks ]

CABLE SELECTION

Q 9.

TWO 150 mm² three core X90 insulated, sheathed and armoured copper cables, including earthing conductors, are connected in parallel to supply a three phase load.

The cables are protected by a circuit breaker and installed touching directly in the ground at a depth of 0.5m. The thermal resistivity of the soil is 1.2(C.m/W.

(i) Neglecting voltage drop, what is the TOTAL maximum current carrying capacity of the cables which form the circuit?

(ii) What would be the effect on the TOTAL current carrying capacity if the cables were spaced 150mm apart?

Table numbers and calculations must be shown to obtain full marks.

(i) Answer....................................................

(ii) Answer..............................................................................................................................

...............................................................................................................................................

[3+3+2= 8 Marks]

DC CIRCUITS

Q 10.

The following values apply to the diagram above -

The voltage across points P and N = 100V

A is 50 Ω ; B is 140 Ω ; C is 90 Ω and  D is 30 Ω.

Calculate:

- the current flowing through resistor C

- the power dissipated in resistor A

All calculations must be shown to obtain full marks

Answers   Current.............................    Power...................................

[2+2 = 4 Marks]

MAXIMUM DEMAND

Q 11.

Calculate the Maximum Demand of a 230V sub-main supplying a distribution board in a domestic installation.

The load connected to the switchboard is:-

- 2 circuits of 12 - 10A socket outlets

- 2 circuits of 2 - 20A socket outlets

- 3 circuits of 12 - lighting points.

All relevant Table numbers and calculations must be shown to obtain full marks.

Answer................................................

[2+2+2+2 = 8 Marks]

VOLTAGE DROP

Q 12.

In a 400/230V, 3 phase industrial installation, a 3 phase 14A drying oven which operates continuously is supplied from a subcircuit originating at a distribution board.

All the cables are:-

- V75 multi-core insulated and sheathed cables with circular copper conductors

- protected by circuit breakers

- not installed with other cables

The circuit details are:-

| Consumer Mains | MD current | 55A |
| --- | --- | --- |
|  | Length | 11m |
|  | Size | 16mm2 |
| Submains | MD current | 36A |
|  | Length | 42m |
|  | Size | 10mm2 |
| Final subcircuit | Length | 25m |
|  | Size | 4mm2 |
|  | The final subcircuit cables have an operating temperature of 60oC |

- Determine the voltage at the oven supply terminals

- Does this comply with the Wiring Rules?

All relevant Table numbers and calculations must be show to obtain full marks

Answer (a) ……………………….                      Answer (b) ………………………

[2+2+2+2+2 = 10 marks]

OVERLOAD & SHORT CIRCUIT CALCULATIONS

Q 13.

What are the minimum and maximum tripping times for a 10A Type C miniature over-current circuit breaker which is subjected to an over-current of 60A?

Overcurrent  divided by MCB Current Rating

Answer   Minimum time..........................	Maximum time............................

[2+2+2 = 6 Marks]

Q 14.

The main switchboard of a 400/230V industrial installation is directly supplied from a 500KVA transformer which has a prospective fault current of 13,990A per phase.

Submains supply a distribution board from the main switchboard.

The following information is known:-

    - Impedance of the Consumers Mains   = 0.0040 Ω

    - Impedance of the Submains cables     = 0.025 Ω

Determine the prospective fault current at:-

(i)  the main switchboard; and

(ii) the distribution board.

Work impedances to 5 decimal places.

All calculations must be shown to obtain full marks.

Answers	MainSw/Bd...................................	Dist/Bd............................................

[2+2+2 = 6 Marks]

RESIDUAL CURRENT DEVICES

Q 15.

A 30 ma RCD is to be installed in the sub-main supplying a distribution board.

- The calculated maximum demand of the sub-main is 25A.

- There are three final sub-circuits supplied from the distribution board.

- The circuits are protected by an 8A, a 16A and a 30 A circuit breakers.

What is the MINIMUM current rating for the RCD?.

Answer........................................

[6 Marks]

MOTORS AND STARTERS

Q 16.

CIRCLE the letter in front of the statement you consider to be the most correct.

On start up, a 3 phase 400V squirrel cage induction motor with an automatic star/delta starter:-

A    starts on half the line voltage (200V).

B    changes to delta connection at about 80% of the motor’s full rated speed.

C    has a starting torque three times that of the DOL starting torque.

D    has a starting current one half of the DOL current.

[4 Marks]

CODE OF PRACTICE

Q 17.

You must supply answers to parts (i) and (ii) to obtain full marks

(i) Unless proven to be de-energised, all electrical equipment must be treated as what?

............................................................................................................................................

(ii) Code Clause number...............................................

[ 2 + 2 = 4 Marks ]

# Text boxes

C

A

B

D

P

N